MB.LV.seco cable datasheet

MB.LV.seco cable is the cable that powers the ten Sector Collector (SC) crates from the A3100 modules. There are a total of 10 cables, one per SC crate.

| MB.LV.seco | (Cristina Fernandez) |  |  |
| --- | --- | --- | --- |
| PRR @ EDMS | Description | Size [mm] | GRAND TOTAL |
|  | LV Sector Collector Cable |  | 10 cables |
| Cable Listing |  |  |  |
|  | Label | Source | Destination |
| 1 | MB.LV.seco @ X2J21/1 : X2J22/1 | X2J21 | X2J22 |
| 1 | MB.LV.seco @ X2J21/2 : X2J22/2 | X2J21 | X2J22 |
| 1 | MB.LV.seco @ X2J11/1 : X2J12/1 | X2J11 | X2J12 |
| 1 | MB.LV.seco @ X2J11/2 : X2J12/2 | X2J11 | X2J12 |
| 1 | MB.LV.seco @ X2J01/1 : X2J02/1 | X2J01 | X2J02 |
| 1 | MB.LV.seco @ X2J01/2 : X2J02/2 | X2J01 | X2J02 |
| 1 | MB.LV.seco @ X2V11/1 : X2V12/1 | X2V11 | X2V12 |
| 1 | MB.LV.seco @ X2V11/2 : X2V12/2 | X2V11 | X2V12 |
| 1 | MB.LV.seco @ X2V21/1 : X2V22/1 | X2V21 | X2V22 |
| 1 | MB.LV.seco @ X2V21/2 : X2V22/2 | X2V21 | X2V22 |

It is made of:

Power wires:

- 2 flexible copper cables 25 mm2 light blue (SCEM 04.08.61.356.1) for 5 V.

- 2 flexible copper cables 25 mm2 black (SCEM 04.08.61.354.3) for 0 V.

- 5V connector: 2 REMA 80188-00 red housing 75 A with REMA 78265-00 contacts

- 0V connector: 2 REMA 80188-02 black housing 75 A with REMA 78265-00 contacts

Sense wires:

- 1 flexible copper cable 0x25 mm2 violet (SCEM 04.01.61.320.5) for sensor 5V.

- 1 flexible copper cable 0x25 mm2 yellow/green (SCEM 04.01.61.416.8) for sensor 0V.

- Connector on the SC crate side: plugs DIN 3 pin PREH 71430-030/0800

- Connector Power supply side: 4 ways Tyco Electronics AMP 280359 with Tyco Electronics AMP 181270-2 contacts.

Shielding:

- 1 flexible copper cable 0x50 mm2 white (SCEM 04.01.61.680.4).

- Tinned copper screen sheath 20 mm diameter (SCEM 04.01.33.180.6)

The copper cable is soldered to the screen sheath on both sides of the cable.

Outer sheath:

- 38.1 mm PRO POWER (SP381/5/BLUE) blue heat shrink

POWER SUPPLY SIDE:

SC CRATE SIDE:

# DETAILED TECHNICAL INFORMATION

POWER WIRES

- 2 flexible copper cables 25 mm2 light blue (04.08.61.356.1) for 5 V.

- 2 flexible copper cables 25 mm2 black (04.08.61.354.3) for 0 V.

Description:

- Specification: LO-GE N° 358

- Conductor: Copper - class 5

- Insulation: EVA

- Rated input voltage: U = 0.5 kV r.m.s.

- Temperature range: -50 to + 150°C

- ACCORDING TO SAFETY INSTRUCTION IS 23

POWER CONNECTOR:

- 5V connector: 2 REMA 80188-00 red housing 75 A with REMA 78265-00 contacts

- 0V connector: 2 REMA 80188-02 black housing 75 A with REMA 78265-00 contacts

Manufacturer: REMA

Order Code (Farnell): 1122504 (black), 1122505(red)

Manufacturer Part No: 80188-02 (black), 80188-00 (red)

#### Description

- HOUSING 75 AMPS BLACK/RED

- Connector type: Rectangular

- Ways, No. of:1

- Material, contact: Copper

- Plating, contact: Silver

- Series: MC

- Current rating:75A

- Poles, No. of:1

- Voltage rating, AC:600V

- Voltage, working: 600V

- AWG 6

SENSE WIRES:

- 1 flexible copper cable 0x25 mm2 violet (04.01.61.320.5) for sensor 5V.

- 1 flexible copper cable 0x25 mm2 yellow/green (04.01.61.416.8) for sensor 0V.

Description:

- Conductor: Tinned copper

  - Construction: 19 X 0.15 mm dia.

  - Dia. 0.66 mm

  - Cross-section: 0.25 mm2

- Insulation: SILTEM

  - o.d. 1.50 mm

- Specification: Rated voltage: 380 V r.m.s.

  - Test voltage: 3500 V r.m.s.

  - Maximum operating temperature: -40 to +125 °C

- ACCORDING TO SAFETY INSTRUCTION IS 23

SENSOR CONNECTOR SC CRATE SIDE:

- Connector on the SC crate side: plugs DIN 3 pin PREH 71430-030/0800

Manufacturer: PREH

Manufacturer Part No: 71430-030/0800

#### Description

- PLUG, DIN, 3PIN

- Connector type: Audio, DIN

- Gender: Plug

- Ways, No. of:3

- Mounting type: Cable

- Contacts, No. of:3

- Current rating:3A

- Diameter, cable max:5.5mm

- Length / Height, external:60mm

- Poles, No. of:3

- Voltage rating, AC:34V

- Current, DC max:3A

- Diameter, body:20mm

SENSOR CONNECTOR POWER SUPPLY SIDE:

- Connector Power supply side: 4 ways socket Tyco Electronics AMP 280359

Manufacturer: TYCO ELECTRONICS / AMP

Manufacturer Part No: 280359

#### Description:

- RECEPTACLE HOUSING, 4WAY

- Connector type: Rectangular

- Gender: Receptacle

- Ways, No. of:4

- Termination method: Crimp

- Series: AMPMODU

- Connector insert type: Female

- Contact style: Socket

- Mounting type: PC Board

- Colour: Black

- Flammability rating:UL94V-1

- Material: Thermoplastic (PPO)

- Temp, op. max:+80°C

- Temp, op. min:-40°C

- Pitch:2.54mm

SENSOR CONNECTOR POWER SUPPLY SIDE CONTACTS:

- Tyco Electronics AMP 181270-2 contacts.

Manufacturer: TYCO ELECTRONICS / AMP

Manufacturer Part No: 182206-2

#### Description:

- CONTACT SOCKET, TIN, 26-22AWG

- Series: AMPMODU

- Connector type: Contact, Crimp

- Gender: Socket

- Termination method: Crimp

- Material, contact: Phosphor Bronze

- Plating, contact: Tin

- Wire size, AWG:22AWG

- Area, wire size min:0.15mm²

- Area, wire size max:0.4mm²

- Diameter, cable max:1.55mm

- Diameter, cable min:1mm

- Wire size, AWG max:22AWG

- Wire size, AWG min:26AWG

COPPER SHEATH

- Tinned copper screen sheath 20 mm diameter (04.01.33.180.6)

Description:

- Conductor: Tinned copper on disposable core

- Nominal diameter: 20 mm

- Sheath diameter: 17-22 mm

- Composition 324 wires of 20/100

- Type: 12317

SHIELDING CONNECTION CABLE:

- 1 flexible copper cable 0x50 mm2 white (04.01.61.680.4).

Description:

- Conductor: Tinned copper

  - Construction: 19 x 0.19 mm dia.

  - Dia.   1.0 mm

  - CROSS-SECTION  0.50 mm2

- Insulation: SILTEM

  - o.d.  1.80 mm

- Specifications: Rated Voltage: 380 V r.m.s.

  - Test Voltage: 3500 V r.m.s.

  - Max. Operating Temperature: -40 to + 125°C

- ACCORDING TO SAFETY INSTRUCTION IS 23

HEAT SHRINK

- 38.1 mm PRO POWER (SP381/5/BLUE) blue heat shrink

Manufacturer: PRO POWER

Manufacturer Part No: SP381/5/BLUE.

#### Description:

- HEAT SHRINK, 38.1MM BLUE 5M

- Diameter, unshrunk:38.1mm

- Diameter, fully shrunk:19mm

- Ratio, shrink:2:1

- Material: Irradiated Polyolefin

- Colour: Blue

- Temperature, shrink:100°C

- Approval Bodies: UL

- Approval category:UL224

- Dielectric strength:20kV/mm

- Flammability rating:VW-1

- Length, Reel (Metric):5m

- Standard: CSA, LR54949

- Temp, op. max:135°C

- Temp, op. min:-55°C

# Text boxes

Pin 3

(5V) violet

Pin 1

(0V) yellow/green

Pin 2 (5V) violet

Pin 3 (0V) yellow/green

Heat Shrink tube

Shielding

LENGHT

YB+1, YB+2:

SC top = 2 meters

SC bottom = 1,5 meters

YB-2, YB-1, YB0:

SC top = 2,5 meters

SC bottom = 2 meters

x2

x2

x2

x2

Sensor connector

SC crate side

Sensor connector

LV module side

LV Module side

SC crate side